## Modbus Funtion & Exeption Code
Modbus funtion support |  | Modbus exception code
Code | Name | code | name
0x01 | Read coils | 0x01 | ILLEGAL FUNTION
0x02 | Read descrete inputs | 0x02 | ILLEGAL DATA ADDRESS
0x03 | Read Holding registers | 0x03 | ILLEGAL DATA VALUE
0x04 | Read input registers | 0x04 | SERVER DEVICE FAILURE
0x05 | Write single coil | 0x05 | ACKNOWLEDGE
0x06 | Write single regitser | 0x06 | SERVER DEVCE BUSY
0x0F | Write multi coils | 0x08 | MEMORY PARITY ERROR
0x10 | Write multi registers

## Modbus Registers Map
register map
Discrete output coils
desription | read/write ouput register status
funtrion support | 0x01, 0x05, 0x06
Address Register | Register parameter |  |  | Modbus protocol start address (hex)
| Parameter | Units | Format | Hi byte | Lo byte
1 | Digital output 0 | on/off | 1 bit | 0 | 0
2 | Digital output 1 | on/off | 1 bit | 0 | 1
3 | Digital output 2 | on/off | 1 bit | 0 | 2
4 | Digital output 3 | on/off | 1 bit | 0 | 3
5 | Digital output 4 | on/off | 1 bit | 0 | 4
6 | Digital output 5 | on/off | 1 bit | 0 | 5
7 | Digital output 6 | on/off | 1 bit | 0 | 6
8 | Digital output 7 | on/off | 1 bit | 0 | 7
Discrete input contacts
desription | read only input register status
funtrion support | 0x02
Address Register | Register parameter |  |  | Modbus protocol start address (hex)
| Parameter | Units | Format | Hi byte | Lo byte
10001 | Digital input 0 | on/off | 1 bit | 0 | 0
10002 | Digital input 1 | on/off | 1 bit | 0 | 1
10003 | Digital input 2 | on/off | 1 bit | 0 | 2
10004 | Digital input 3 | on/off | 1 bit | 0 | 3
10005 | Digital input 4 | on/off | 1 bit | 0 | 4
10006 | Digital input 5 | on/off | 1 bit | 0 | 5
10007 | Digital input 6 | on/off | 1 bit | 0 | 6
10008 | Digital input 7 | on/off | 1 bit | 0 | 7
Analog input registers
desription | read only input register value
funtrion support | 0x04
note | 0<= value <= 10000
Address Register | Register parameter |  |  | Modbus protocol start address (hex)
| Parameter | Units | Format | Hi byte | Lo byte
30001 | Analogl input 0 | mV | 16 bit | 0 | 0
30002 | Analogl input 1 | mV | 16 bit | 0 | 1
30003 | Analogl input 2 | mV | 16 bit | 0 | 2
30004 | Analogl input 3 | mV | 16 bit | 0 | 3
Analog output holding registers
desription | read / write output register value
funtrion support | 0x01, 0x0F, 0x10
note | 0<= value <= 10000
Address Register | Register parameter |  |  | Modbus protocol start address (hex)
| Parameter | Units | Format | Hi byte | Lo byte
40001 | Analogl output 0 | mV | 16 bit | 0 | 0
40002 | Analogl output 1 | mV | 16 bit | 0 | 1

## Data format
describe the data format of the function
Function: 0x01 - Read coils
| Byte | description
req
| 0 | start address, high byte
| 1 | start address, low byte
| 2 | quantity of coils, high byte
| 3 | quantity of coils, low byte
res
| 0 | byte count
| 1 | coil status
| … | coil status
| n | coil status
Function: 0x02 - Read descrete input
| Byte | description
req
| 0 | start address, high byte
| 1 | start address, low byte
| 2 | quantity of inputs, high byte
| 3 | quantity of inputs, low byte
res
| 0 | byte count
| 1 | input status
| … | input status
| n | input status
Function: 0x03 - Read holding registers
| Byte | description
req
| 0 | start address, high byte
| 1 | start address, low byte
| 2 | quantity of registers, high byte
| 3 | quantity of registers, low byte
res
| 0 | byte count
| 1 | register value, high byte
| 2 | register value, low byte
| … | …
Function: 0x04 - Read input registers
| Byte | description
req
| 0 | start address, high byte
| 1 | start address, low byte
| 2 | quantity of registers, high byte
| 3 | quantity of registers, low byte
res
| 0 | byte count
| 1 | register value, high byte
| 2 | register value, low byte
| … | …
Function: 0x05 - write single coil
| Byte | description
req
| 0 | address of coil, high byte
| 1 | address of coil, low byte
| 2 | status on: =0xFF, off =0x00
| 3 | 0x00
res
| 0 | address of coil, high byte
| 1 | address of coil, low byte
| 2 | status on: =0xFF, off =0x00
| 3 | 0x00